SECTION 732 - ITS AND ELECTRICAL DEVICES INSTALLATION

##This section cross-references Sections 610, 611, 614, 731, 733, 734, 735 and 736.

If any of the above sections are relevant, they should be included in the specification.

If any of the above sections are not included in the specification, all references to those sections should be struck out, ensuring that the remaining text is still coherent:

##Sections 731, 733, 734, 735 and 736 should be included in the specification:

732.01 GENERAL

(a) Scope

This section covers the requirements for the installation of ITS Devices and other ‘on-road’ electrical devices within the state of Victoria for works supervised by VicRoads. This document shall be read in conjunction with VicRoads TCS series specifications, TC series Standard Drawings and individual contract documents.

For the purpose of this specification, ITS devices and ‘on-road’ electrical devices shall include:

(i) traffic signals

(ii) road lighting

(iii) ramp control/metering signs

(iv) variable message signs

(v) electronic speed limit signs

(vi) ice warning stations

(vii) electrical distribution cabinet

(viii) freeway data station

(ix) lane use signs

(x) ITS field cabinets

(xi) UPS

(xii) freeway ramp signals

(xiii) digital CCTV

(xiv) over height detection systems

(xv) Bluetooth data stations

(xvi) travel time signs

(xvii) side road activated speed systems

(b) General requirements

The Contractor shall be responsible for the installation and commissioning of all devices covered under this specification in accordance with individual contract documents.

(c) Prequalified contractor

All works associated with the installation and commissioning of all devices covered under this specification shall be undertaken by contractors that are appropriately prequalified as detailed in Table 732.011 below.

**Table 732.011 Contractor prequalification level requirements**

|  |  |
| --- | --- |
| **Conduits and pits for:** | **Prequalification level** |
| Works on or associated with traffic signals | STS1 |
| All other on-road electrical works | STCE |
| Works associated with VicRoads owned communications networks | STCE |
| Works associated with CCTV or telecommunications carrier networks | SCTV  (must hold AMCA license) |
| Works associated with ‘in-pavement detector installation (includes inductive loops and wireless in-pavement vehicle sensors) | SVDL |

Subcontractors undertaking works covered under this specification shall be prequalified at the appropriate level under the VicRoads contractor prequalification scheme, in the subcontractors own right.

**©** Department of Transport May 2019

Section 732 (Page 1 of 15)

732.02 REFERENCED AND RELATED SPECIFICATIONS, STANDARDS AND DRAWINGS

All works associated with the installation and commissioning of all devices covered under this specification shall conform to all relevant VicRoads specifications, VicRoads standard contract sections and Australian Standards.

All works associated with the installation and commissioning of all devices covered under this specification shall conform to the general requirements of:

(a) VicRoads ‘TCS’ series specifications

(b) VicRoads ‘TC’ series standard drawings

(c) AS/NZS 3000 Wiring Rules

(d) Victorian Service and Installation Rules.

The individual requirements of the Victorian Electricity Supply Industry (VESI) and the local electricity distribution business shall apply for matters relating to the provision of mains power.

Australian Standards referred to in this section are listed in Table 732.021 below.

**Table 732.021 List of Australian Standards**

|  |  |
| --- | --- |
| **Australian Standard** | **Title** |
| AS/NZS 3000 | Wiring Rules |

VicRoads Specifications and Technical Notes referred to in this section are listed in Table 732.022 below.

**Table 732.022 List of specifications and Technical Notes**

|  |  |
| --- | --- |
| **Specification number** | **Title** |
| TCS 003 | Supply of Ramp Control / Metering Signs |
| TCS 015 | Variable Message Signs |
| TCS 037 | Electronic Speed Limit Signs |
| TCS 039 | Ice Warning Stations |
| TCS 043 | The Supply of Electrical Distribution Cabinets |
| TCS 048 | Freeway Data Stations |
| TCS 056 | Lane Use Signs |
| TCS 057 | Active Advanced Warning System for Railway Level Crossings |
| TCS 058 | UPS for traffic signals |
| TCS 061 | ITS Field Cabinet |
| TCS 063 | Installation of Freeway Ramp Signals |
| TCS 067 | Digital CCTV Camera |
| TCS 068 | Over-height Detection System |
| TCS 069 | Supply and Installation of Bluetooth Data Stations |
| TCS 070 | Travel Time Signs |
| TCS 071 | The Supply and Installation of Side Road Activated Speeds (SRAS) |

**©** Department of Transport May 2019

Section 732 (Page 2 of 15)

VicRoads standard sections referred to in this section are listed in Table 732.023 below.

**Table 732.023 List of standard sections**

|  |  |
| --- | --- |
| **Standard section** | **Title** |
| 610 | Structural concrete |
| 611 | Steel reinforcement |
| 614 | Formwork |
| 730 | Traffic Signal Installation |
| 731 | Road Lighting Installation |
| 733 | Conduits and Pits for Underground Wiring and Cabling |
| 734 | Electrical Network Installation |
| 735 | Communications Network Installation |
| 736 | ITS Device Testing and Integration |

VicRoads Standard Drawings referred to in this section are listed each device specific clause within this section.

*NOTE: VicRoads Standard Drawings, specifications and guidelines are available for downloading from VicRoads website*

732.03 GENERAL REQUIREMENTS

The installation of new ITS devices or additional works at an existing ITS installation by the Contractor shall include:

(a) supply and installation of civil works including, but not limited to, trenching, under road bores, draw strings, slabs, distribution cabinet foundations, and pole foundations

(b) supply and installation of all electrical works including, but not limited to, conduits, conduit bends, cable pits and lids

(c) liaison with the local power distribution company and relevant authorities for the installation of the works, and the obtaining of all necessary approvals and permits from the relevant authorities

(d) supply, installation and connection of all hardware, equipment and materials including, but not limited to, the distribution Board, circuit breakers, poles, brackets, ITS devices, electrical cables, cable guards, fuses, fittings and all materials and equipment necessary to complete and commission the installation

(e) testing and integration of all installed devices in accordance with Section 736

(f) reinstatement of all works.

732.04 ASSET OWNERSHIP

The Principal will retain ownership of the ITS installation. The Contractor is not authorised to sign any document with any party which transfers ownership of the installation to any other party.

Furthermore, the Contractor is not authorised to sign or enter into any agreement with any electricity distribution business, electricity retailer or other party on behalf of the Principal for supply of power to the installation.

**©** Department of Transport May 2019

Section 732 (Page 3 of 15)

732.05 PITS AND CONDUITS

(a) General

Pits and conduits shall be installed in accordance with Section 733 and individual contract documents.

Separate power and communications conduits shall be used to connect to all ITS devices.

(b) Managed motorways

Trunk conduit networks for managed motorways shall be installed in accordance with relevant standard drawings and individual contract documents.

As a minimum, the number of conduits shall be 2 x 100 mm electrical conduits and 2 x 100 mm communications conduits on both sides of the freeway.

(c) Arterial roads

Conduit networks for arterial roads shall be installed in accordance with relevant standard drawings and individual contract documents.

As a minimum, the number of conduits shall be 1 x 100 mm electrical conduit and 1 x 100 mm communications conduit on one side of the roadway.

732.06 FOUNDATIONS

Standard foundations shall comply with all relevant standard drawings and, where required, approved engineering drawings.

Where required, non-standard foundation designs for ITS device support structures shall be proof engineered and approved by the superintendent.

The location of all existing underground and above ground services shall be proven and confirmed on site by the Contractor before commencement of any works.

732.07 CABLING

(a) Cabling for mains power

All mains power cabling shall be fully compliant with the Wiring Rules and Section 734.

The specific requirements for mains power cabling and architecture shall be detailed in individual contract documents.

(b) Communications cabling

All communications cabling shall comply with Section 735.

The specific requirements for communications cabling and architecture shall be detailed in individual contract documents.

732.08 TRAFFIC SIGNALS

The Contractor shall supply and install traffic signals in accordance with Section 730.

**©** Department of Transport May 2019

Section 732 (Page 4 of 15)

732.09 ROAD LIGHTING

The Contractor shall supply and install road lighting in accordance with Section 731.

Where an existing lighting scheme is being added to, or upgraded, all existing circuits that do not meet the current requirements of Section 731 or the current version of AS/NZS 3000, shall be decommissioned and replaced or upgraded to current standards.

In addition to the requirements of Section 731, where a lighting pole is installed within a barrier (e.g. a concrete or steel barrier) an additional in-line fuse shall be installed in the cable located behind the poles access door.

732.10 RAMP CONTROL / METERING SIGNS

(a) Sign requirements

The Contractor shall only supply and install VicRoads Type Approved Ramp Control/Metering Signs.

The installation of the signs shall comply with the installation requirements of TCS 003 and the following.

(b) Foundations

Foundations shall comply with the following standard drawings;

**Table 732.101 Standard drawings for RC3 /TT3 foundations**

|  |  |
| --- | --- |
| **Drawing number** | **Title** |
| TC-2223 | RC3 Pole – Typical Arrangement |
| TC-2235 | RC3 Pole Spread Foundation Type 1 – Typical Arrangement |
| TC-2236 | RC3 Pole Spread Foundation Type 2 – Typical Arrangement |

**HP No concrete shall be poured for any foundation before inspection and approval by the superintendent.**

(c) Mounting

RC signs shall be mounted on the nominated pole type unless approved by the Superintendent.

A typical mounting arrangement for an RC3 sign is shown in the following standard drawing.

**Table 732.102 Standard drawings for RC3/TT3 pole**

|  |  |
| --- | --- |
| **Drawing number** | **Title** |
| TC-2224 | RC3 / TT3 Pole Mounting Arrangement – Typical Arrangement |

Under no circumstances shall the following poles be used to mount any RC signs:

* slip base street lighting poles
* impact absorbing poles
* mid-hinge poles.

Sign positions shall be nominated in individual contract documents.

**©** Department of Transport May 2019

Section 732 (Page 5 of 15)

(d) Connection to power

The connection to power shall be nominated in individual contract documents.

Unless otherwise specified in individual contract documents, the connection to power for each RC sign type shall be as per Table 732.103 below.

**Table 732.103 Point of supply requirements**

|  |  |
| --- | --- |
| **Sign type** | **Point of supply** |
| RC1-A | Where associated with a traffic signal installation, the power shall be from the associated traffic signal controller.  **Under no circumstances** shall the sign be powered from a separate point of supply when installed on a traffic signal pedestal.  Where no traffic signals exist, a new or other existing point of supply shall be used. |
| RC2-A | The associated freeway ramp signal controller |
| RC2-C | The associated freeway ramp signal controller |
| RC3-A | The associated traffic signal controller or a new point of supply as specified in individual contract documents. |
| RC3-C | As specified in individual contract documents |

732.11 VARIABLE MESSAGE SIGNS

(a) Sign requirements

The Contractor shall only supply and install VicRoads Approved VMS in accordance with any relevant sign requirements as specified in TCS 015.

Sign positions shall be nominated in individual contract documents.

(b) Mounting structure

The type of mounting structure shall be detailed in individual contract documents.

Where required, the mounting structure shall be designed and proof engineered to suit the VMS and any other assets being installed on the structure.

Typical arrangements for the VMS attached to an accessible gantry are shown in the following standard drawings.

**Table 732.111 Standard drawings for VMS on accessible gantry**

|  |  |
| --- | --- |
| **Drawing number** | **Title** |
| TC-2270 | Typical Arrangement |
| TC-2273 | Typical Conduit Route – Sheet 1 of 6 |
| TC-2274 | Typical Conduit Route – Sheet 2 of 6 |
| TC-2275 | Typical Conduit Route – Sheet 3 of 6 |
| TC-2276 | Typical Conduit Route – Sheet 4 of 6 |
| TC-2277 | Typical Conduit Route – Sheet 5 of 6 |
| TC-2278 | Typical Conduit Route – Sheet 6 of 6 |
| … table continued next page | |

**©** Department of Transport May 2019

Section 732 (Page 6 of 15)

**Table 732.111 Standard drawings for VMS on accessible gantry** (continued from previous page)

|  |  |
| --- | --- |
| **Drawing number** | **Title** |
| TC-2279 | Typical Gantry Leg Cabinet Details |
| TC-2280 | Access Ladder and Cage Details |
| TC-2281 | Access Walkway and Handrail – 1 of 4 |
| TC-2282 | Access Walkway and Handrail – 2 of 4 |
| TC-2283 | Access Walkway and Handrail – 3 of 4 |
| TC-2284 | Access Walkway and Handrail – 4 of 4 |
| TC-2285 | Cladding Details |
| TC-2286 | Foundation Conduit Details |
| TC-2287 | Typical Gantry Earthing Arrangement |
| TC-2288 | Electrical and Communications Cable Connections Details |
| TC-2289 | Leg Security Mesh – Typical Arrangement |

(c) Foundations

The foundations shall be designed and proof engineered to suit the mounting structure being installed.

(d) Sign alignment

VMS shall be aligned such that the active displays are clearly visible to approaching traffic in 100 m to 300 m.

(e) Connection to power

The connection to power shall be nominated in individual contract documents.

732.12 ELECTRONIC SPEED LIMIT SIGNS

(a) Sign requirements

The Contractor shall only supply and install VicRoads Type Approved ESLS.

The installation of the signs shall comply with the installation requirements of TCS 037 and the following.

The type and size of ESLS shall be specified in individual contract documents.

(b) Poles

The pole shall be designed and engineered to support the sign and, where required, a solar panel and associated control equipment and batteries.

Poles on managed motorways shall be designed in accordance with standard drawing TC‑2220.

**©** Department of Transport May 2019

Section 732 (Page 7 of 15)

(c) Foundations

(i) Foundations on managed motorways shall be designed in accordance with standard drawing TC‑2233. ESLS on managed motorways shall be a LUS in accordance with clause 732.16.

(ii) Foundations on other roads shall be designed according to sign size and other attached equipment.

**HP No concrete shall be poured for any foundation before inspection and approval by the superintendent.**

(d) Signs

ESLS shall be installed on an approved post.

Sign positions shall be nominated in individual contract documents.

(e) Connection to power

The connection to power shall be nominated in individual contract documents.

732.13 ICE WARNING STATIONS

This clause is currently under review.

732.14 ELECTRICAL DISTRIBUTION CABINETS

(a) Cabinet

The Contractor shall only supply and install VicRoads Type Approved Electrical Distribution Cabinet.

The installation of the DB shall comply with the installation requirements of TCS 043 and the following.

The type of DB required shall be nominated in individual contract documents.

Unless specifically approved by the Superintendent, each site or installation shall include one only distribution cabinet.

Where an existing distribution cabinet does not have sufficient spare capacity for additional assets, a new distribution cabinet with sufficient capacity shall replace the existing distribution cabinet.

Where a new cabinet replaces an existing cabinet, the existing cabinet and foundation shall be decommissioned and removed from site.

(b) Foundations

Foundations shall comply with the installation requirements of TCS 043 and the standard drawings detailed in Table 732.141 below.

All concrete works shall conform to VicRoads standard drawings and be undertaken in accordance with Sections 610, 611, and 614.

**©** Department of Transport May 2019

Section 732 (Page 8 of 15)

**Table 732.141 Standard drawings for distribution cabinet foundations**

|  |  |  |
| --- | --- | --- |
| **DB Type** | **Location** | **Drawing** |
| 1 | Managed Motorway or Freeway | TC-2231 |
| 1 | Arterial Road | TC-1062 |
| 2 | Arterial Road  (Not used on managed motorways or Freeways) | TC-1074 |
| 3 | Managed Motorway or Freeway  (Not used on arterial roads) | TC-2232 |

**HP No concrete shall be poured for any DB foundation or apron before inspection and approval by the Superintendent.**

732.15 FREEWAY DATA STATIONS

Freeway data stations shall be installed in accordance with the installation requirements of the device manufacturer.

Some typical installation arrangements are shown in the standard drawings detailed in Table 732.111

**Table 732.151 Standard drawings for freeway data stations**

|  |  |
| --- | --- |
| **Drawing number** | **Title** |
| TC-2297 | TIRTL In-barrier – Typical installation |
| TC-2298 | TIRTL In-kerb – Typical installation |

732.16 LANE USE SIGNS

(a) Sign requirements

The Contractor shall install VicRoads Type Approved LUS. The installation of the signs shall comply with the installation requirements of TCS 056 and the following.

Unless otherwise specified in individual contract documents, all LUS shall be "C” size.

(b) Non-accessible gantry installation

Signs installed on gantry shall be positioned so that each sign is located directly above each associated lane.

Installation of signs on non-accessible gantries shall be in accordance with the following standard drawings.

**©** Department of Transport May 2019

Section 732 (Page 9 of 15)

**Table 732.161 Standard drawings for LUS on non-accessible gantry**

|  |  |
| --- | --- |
| **Drawing number** | **Title** |
| TC-2260 | General Arrangement |
| TC-2261 | Internal Conduiting and Mounting Arrangement |
| TC-2262 | Gantry Leg Cabinet |
| TC-2263 | Column Base Plate Details |
| TC-2264 | Foundation Conduit Details |
| TC-2265 | Typical Gantry Earthing Arrangement |
| TC-2266 | Electrical and Communications Cable Connections Details |
| TC-2267 | Leg Security Mesh – Typical Arrangement |
| TC-2268 | Gantry Leg Access Openings – typical Arrangement |

(c) Accessible gantry installation

Signs installed on gantry shall be positioned so that each sign is located directly above each associated lane.

Installation of signs on accessible gantries shall be in accordance with the following standard drawings.

**Table 732.162 Standard drawings for LUS on accessible gantry**

|  |  |
| --- | --- |
| **Drawing number** | **Title** |
| TC-2270 | General Arrangement |
| TC-2272 | LUS Mounting Arrangements |
| TC-2273 | Conduit Route – 1 of 6 |
| TC-2274 | Conduit Route – 2 of 6 |
| TC-2275 | Conduit Route – 3 of 6 |
| TC-2276 | Conduit Route – 4 of 6 |
| TC-2277 | Conduit Route – 5 of 6 |
| TC-2278 | Conduit Route – 6 of 6 |
| TC-2279 | Gantry Leg Cabinet |
| TC-2280 | Access Ladder and Cage Details |
| TC-2281 | Access Walkway and Handrail – 1 of 4 |
| TC-2282 | Access Walkway and Handrail – 2 of 4 |
| TC-2283 | Access Walkway and Handrail – 3 of 4 |
| TC-2284 | Access Walkway and Handrail – 4 of 4 |
| TC-2285 | Cladding Details |
| TC-2286 | Foundation Conduit Details |
| TC-2287 | Typical Gantry Earthing Arrangement |
| TC-2288 | Electrical and Communications Cable Connections Details |
| TC-2289 | Leg Security Mesh – Typical Arrangement |

**©** Department of Transport May 2019

Section 732 (Page 10 of 15)

(c) Structure installation

Signs installed on other types of structure such as bridges, shall be positioned so that each sign is located directly above each associated lane.

**HP** **The proposed attachment method must be approved by VicRoads Structural Design Team and the Superintendent before any associated works commence.**

Installation of signs on structures shall be in accordance with the following standard drawings.

**Table 732.163 Standard drawings for LUS on a structure**

|  |  |
| --- | --- |
| **Drawing number** | **Title** |
| TC-2310 | Elevation Typical Arrangement |
| TC-2311 | General Arrangement Layout |
| TC-2312 | Mounting Arrangement Type 1 |
| TC-2313 | Mounting Frame Type 1 |
| TC-2314 | Mounting Arrangement Type 2 |
| TC-2315 | Mounting Frame Type 2 |
| TC-2316 | Mounting Arrangement Type 3 |
| TC-2317 | Mounting Frame Type 3 |
| TC-22318 | Anti-Vandal Cowling |
| TC-22319 | Junction Box, Electrical and Communications Cable Connection Detail |

(d) Post mounted installation

Signs installed on posts or pedestals adjacent to lanes (typically operated as ESLS) shall be installed in accordance with the following standard drawings.

**Table 732.164 Standard drawings for LUS on accessible gantry**

|  |  |
| --- | --- |
| **Drawing number** | **Title** |
| TC-2220 | VSLS Pole and Base Plate |
| TC-2233 | VSLS Pole Foundation Concrete |
| TC-2234 | VSLS Pole Spread Footing |

(e) Power

The point of supply (power) shall be from the ITS Field Cabinet housing the LUS Group controller.

732.17 ITS FIELD CABINET

(a) Cabinet

The Contractor shall only supply and install VicRoads Type Approved ITS Field Cabinet.

The installation of the ITS Field Cabinet shall comply with the installation requirements of TCS 061 and the following.

The type of ITS field cabinet required shall be nominated in individual contract documents.

**©** Department of Transport May 2019

Section 732 (Page 11 of 15)

(b) Foundations

Foundations shall comply with the following standard drawings.

**Table 732.171 Standard drawings for ITS field cabinets**

|  |  |
| --- | --- |
| **Drawing number** | **Title** |
| TC-2230 | Single ITS Cabinet Foundation - Typical |
| TC-2237 | Site Layout for ITS Field Cabinets Located on Batters |
| TC-2238 | Pedestrian Safety Fence Arrangements for ITS Field Cabinets - Typical Arrangement |
| TC-2239 | Double ITS Cabinet Foundation - Typical |
| TC-2303 | ITS Field Cabinet Access – Typical Arrangement at Gantries |

**HP No concrete shall be poured for any ITS field cabinet foundation or apron before inspection and approval by the Superintendent.**

(c) Power

The point of supply (power) shall be from the distribution cabinet nominated in individual contract documents.

732.18 UNINTERRUPTABLE POWER SUPPLIES

This clause is currently under review.

732.19 FREEWAY RAMP SIGNALS

(a) Signal lanterns

The Contractor shall install VicRoads Type Approved Traffic Signal Lanterns. The installation of the lanterns shall comply with the relevant installation requirements of Section 730, Contract specific requirements and the following standard drawings.

**Table 732.191 Standard drawings for freeway ramp signals**

|  |  |
| --- | --- |
| **Drawing number** | **Title** |
| TC-2250 | FRS lantern support structures – Cantilever gantry for 2 lanes metered – Sheet 1 of 2 – Typical arrangement |
| TC-2252 | FRS lantern support structures – Portal gantry for 3 or more lanes metered – Sheet 1 of 3 – Typical arrangement |
| TC-2256 | FRS lantern support structures – Beam mounted signal lantern head support assembly – Typical arrangement |
| TC-2257 | FRS lantern support structures – Beam mounted static sign support assembly |
| TC-2258 | FRS lantern support structures – Column mounted signal lantern head support assembly |
| TC-2259 | FRS lantern support structures – Column mounted static sign support assembly |

**©** Department of Transport May 2019

Section 732 (Page 12 of 15)

(b) Ramp signal controller

The Contractor shall install VicRoads Approved Ramp Signal Controller in accordance with the requirements of TCS 063.

(c) Power

The point of supply (power) shall be from the ITS field cabinet housing the ramp signal controller.

732.20 DIGITAL CLOSED CIRCUIT TELEVISION CAMERAS

The Contractor shall only supply and install VicRoads Approved CCTV Cameras.

The installation of CCTV shall comply with the installation requirements of TCS 067 and the following.

(a) CCTV on freeways

CCTV installed on a freeway or managed motorway shall be located as far as is practicable to provide ‑

(i) clear and unimpeded view of all areas of the carriageway and surrounding areas

(ii) clear view of signs (e.g. LUMS) and other roadside infrastructure

(iii) easy access for maintenance works.

The preferred mounting arrangement for CCTV in order of preference is:

(iv) on a mid-hinge camera pole

(v) on a LUMS gantry

(vi) on other structure approved by the Superintendent.

CCTV cameras shall not be located on any pole, gantry or other support structure located on or within a median barrier separating running lanes (e.g. main line and collector/distributor lanes) that would require multiple lane closures for maintenance access.

(b) CCTV on arterial roads

CCTV cameras installed on arterial roads at signalised intersections shall be located as far as is practicable to provide:

(i) clear and unimpeded view of all approaches to the intersection

(ii) easy access for maintenance works.

In some locations, in order to meet the requirements of (i) above, two cameras may be required.

The preferred mounting arrangement for CCTV in order of preference is:

(iii) on a mid-hinge camera pole

(iv) on a JUP, JUMA or MA (attached to the vertical column of the pole)

(v) on a 2B pedestal (attached via a raiser bracket to provide additional height).

CCTV cameras shall not be located on the outreach of a MA or JUMA as this creates access issues for maintenance activities.

732.21 OVER-HEIGHT DETECTION SYSTEM

This clause is currently under review.

**©** Department of Transport May 2019

Section 732 (Page 13 of 15)

732.22 BLUETOOTH DATA STATIONS

The Contractor shall only supply and install VicRoads approved Bluetooth Data Stations (BDS).

The installation of the BDS stations shall comply with the installation requirements of TCS 069.

The number of BDS and the installation location(s) shall be specified in individual contract documents.

732.23 TRAVEL TIME SIGNS

The Contractor shall only supply and install VicRoads Approved Travel Time Signs.

The installation of the signs shall comply with the installation requirements of TCS 070 and the following.

The type of travel time sign(s), the number of signs and the installation location(s) shall be specified in individual contract documents.

732.24 SIDE ROAD ACTIVATED SPEEDS

The Contractor shall only supply and install VicRoads Type Approved SRAS systems.

The installation of the signs shall comply with the installation requirements of TCS 071 and the following.

The number of signs and the installation location(s) shall be specified in individual contract documents.

732.25 LABELLING OF INSTALLED ASSETS

The Contractor shall affix labels to all ITS assets installed under this Contract in accordance with this clause and device specific specifications.

The Contractor shall supply all blank self-adhesive base labels and self-adhesive numbers in accordance with this section. The Contractor shall attach all numbers to the base label, in accordance with the correct matching asset records as supplied to the Contractor.

The Contractor shall thoroughly clean the area to be covered by the label prior to attaching the label and if a liquid cleaning solution is used, ensure that the area is completely dry before application. Any labels that delaminate due to insufficient surface preparation shall be rectified by the Contractor.

732.26 DATA COLLECTION OF ASSETS

ITS installations shall have all required information recorded and provided as specified below.

All ITS assets shall have their location identified and recorded using GPS co-ordinates. The co-ordinates shall be captured using the World Geodetic System WGS84 in decimal degrees to 6 decimal places.

Details of all installed assets (e.g. ITS field cabinets, pole mounted cabinets, signs, data stations, distribution cabinets, circuits, cabling, pits, etc.) shall be recorded in an Excel spreadsheet.

The following general site information shall be provided for every ITS device installed, as applicable:

**©** Department of Transport May 2019

Section 732 (Page 14 of 15)

* device type (e.g. site number)
* site name
* road
* nearest intersection or interchange
* chainage
* municipality
* VicRoads region
* point of supply (e.g. Distribution cabinet or ITS Field cabinet)
* device GPS co-ordinates
* as‑constructed schematic drawings of electrical network and all power circuits
* as‑constructed schematic drawings of communications network.

732.27 REDUNDANT ASSETS

All redundant assets, including foundations, poles, cabinets, etc. shall be removed and disposed of as directed by the Superintendent. Any asset that could be re-used may be required to be delivered to a location nominated by the Superintendent and remain VicRoads property.

As existing public lighting assets may be owned by the local power distribution company, the Contractor shall give consideration to the method of removal of redundant lighting assets and, where required, shall deliver such redundant assets to a location specified by that Power Distribution Company within its area.

732.28 BACKFILLING, RE-INSTATEMENT AND CLEAN-UP WORKS

The Contractor shall comply with the requirements of the Road Opening Permit issued by the relevant authority. Where these requirements are silent, the Contractor shall undertake backfilling in accordance with Section 733 Conduits and Pits for Underground Wiring and Cabling, clause 733.06 Backfilling.

On completion of all excavation and reinstatement works, the Contractor is to ensure that all rubble, surplus crushed rock, surplus pavement materials, surplus concrete and all other surplus materials are removed from the site. The Contractor is to leave the work site in a clean and safe condition.

Subject to the requirements of clause 732.27 above, civil hardware and equipment which is not to be reused or salvaged is to be removed from the site and disposed of by the Contractor and the cost of removal and disposal is to be included in the tender price.

732.29 COMISSIONING, TESTING AND INTEGRATION

Commissioning, testing and integration of all ITS assets shall be carried out in accordance with Section 736 and individual contract specific requirements.

732.30 AS-CONSTRUCTED PLANS

The Contractor shall supply to the Superintendent two copies of ‘As‑constructed’ plans along with a USB drive or other approved storage medium containing the CADD/Microstation drawing files, and the same shall be supplied by the Contractor to the local distribution company if appropriate.

**©** Department of Transport May 2019

Section 732 (Page 15 of 15)